Please complete the text to suit your requirements.

Further information regarding tender specifications:

- The basics for steel frames (see BOS Compendium)

asepticDOOR: The anti-bacterial door system

An entire element with test certificate from the Berlin Search Care GmbH Hygiene Institute

PEFC: 70% PEFC certified   NC-PEFC/COC-000018

Four partners – one solution

Steel frame	BOS Best Of Steel

Door handle	HÄFELE

Door leaf	JELD-WEN

Door surface	RESOPAL® + HIPERCARE®

Verifiable:

- good anti-bacterial effect on all surfaces

- cleaning and disinfectant compatibility

- surfaces can be cleaned quickly and easily

- advisable for hospital hygiene and infection prevention

BOS 2 part wrap around frame as block profile for almost all wall types, encompassing the wall

based on following technical data:

Amount:	...

BOS profile: 	[  ] 15ZBud 	(rebated closing door leaf and single rebate)

[  ] 15ZBsd 	(flush closing door leaf and single rebate)

Design: 	2 part split

single leaf

Material: 	anti-bacterial powder coating, silk gloss

[  ] RAL 9010

[  ] RAL ...

Sheet thickness: 	[  ] 1.5 mm

[  ] 2.0 mm

Measurements:

Structural wall measurement: 	[  ] … 	x … 	mm (maximum 1260 x 2135 mm)

Rebate measurements: 	[  ] … 		x  … 	mm (maximum 1216 x 2108 mm)

Receiving opening: 	[  ] ... 		mm (minimum 150 mm)

Total depth frame:	[  ] 180 	mm

[  ] ... 	mm

Architrave front / back: 	[  ] 30  /  45 	mm

[  ] ...   /  ...  	mm

Backbend front / back: 	[  ] 15  /  15 	mm

[  ] ...   /   ...  	mm

Rebate width: 	15 mm

Rebate depth:

[  ] 28,5 mm, closing level 	[  ] 4,5 	mm 	(standard for rebated door leaf)

[  ] 46,5 mm, closing level	[  ] 17 	mm 	(standard for flush door leaf)

[  ] ...     mm, closing level 	...	mm

Handle height: 	[  ] 1050 	mm

[  ] 850 	mm

[  ] ...      	mm

Stainless steel striking plate:	[  ] Protect & Clean (flush and rebated)

[  ] Protect & Clean with latch adjustment (flush)

Metre mark: 	pre-punched

Foundation bedding: 	[  ] 0 	mm

[  ] 30 	mm

[  ] ...  	mm

Seal: 	TPE hollow chamber seal

Anchor: 	BOS levelling anchor

For on site foaming (please see Notes):

[  ] slotted holes in the seal groove

Hinge pockets: 	2 pieces	
	[  ] DIN right

[  ] DIN left

[  ] BVX11000-3D

[  ] Standard butt hinge radius cornered 102x76x3

Further specifications:

[  ] Snap-off transportation guards (standard for powder coated frames)

[  ] Potential equalisation (earthing)

[  ] Radiation protection: 	[  ] partial lead lining (minimum thickness 1.25 mm)

[  ] full lead lining (minimum thickness 1.25 mm)

Notes:

- Installation should be carried out by experienced personnel!

- For 2 part split frames we recommend intermittent foaming in the area of the hinge pockets.

- Colour deviations in powder coating, in particular in metallic paints, between elements powder 
  coated in the same colour can occur. These are due to the different subsurfaces and no liability 
  can be derived.

Recommendations:

- For stud walls with a width >1000 mm, choose a material strength of 2 mm (high rigidity).

- For brick walls choose a frame receiving opening 3-5mm larger than the actual requirement                 
  (tolerance compensation).

- Seal any gaps occuring between the wall and the frame with acrylic.

LEED- und DGNB Criteria:

BOS Best Of Steel combines frame design with sustainable building. BOS steel frames in various designs can be found in the product databank of greenbuildingproducts.eu, which have been  evaluated according to LEED and DGNB criteria.

Architect Consulting Service: architekten@BestOfSteel.de

JELD-WEN Door Leaf Optima 30

Door leaf with measurements according to DIN 18101:

Surface:	Resopal 0,8 mm Hipercare, according to door range

Core:	Climate class II, tubular chipboard inlay

Door leaf:                                 40 mm

Lipping:                                    Lipping 3 mm, climate class II,

door thickness approx. 39 mm - from HPL 0,5 mm

Framework:	Concealed edge TS 40-54 mm  wood/

wood material 3 sides

Reinforcement:	Stress group "M"

Edge:	Edge coating on 3 sides  (as surface)

within JELD-WEN edge range

Rebate:	Standard rebate 13,0 x 25,5 mm, 3 sided

Lock:	PZ lock, class 4, stainless steel with whisper latch

Hinges:	2, stainless steel surface

[  ] VX 7939/160 (rebated door leaf)

[  ] VX 7929/160 (flush door leaf)

Handle:	Häfele handle, U form, PZ rosette,

stainless steel Alasept coating

Jeld-Wen combines components with additional door features such as fire, smoke and sound  protection as well as wetroom suitability, radiation protection and many other features.